## Incomer 4000A
BACK TO INDEX
Incomer 4000A
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Remarks | Vendor Comments dt:
ACB | 4000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos |  | 4000A, 65kA, FP, MIC6.0E, ACB – MTZ Active‐ MTZ240H16.0E4PED
| 4000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos |  | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | As per scheme |  |  | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos |  | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos |  | If required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
CT PT | Current Transformer | CT CTR: 4000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set |  | CT CTR: 4000/1A , Cl‐0.5, 20VA Resin cast ‐ metering
| Current Transformer | CT CTR: 4000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set |  | CT CTR: 4000/1A, CL ‐ 5P20, 20VA Resin cast for Protection Relay
| Current Transformer | CT CTR: 4000/1A, CL - PS, 20VA Resin cast for REF Relay | Kalpa | 1 | Set |  | CT CTR: 4000/1A, CL ‐ PS, 20VA Resin cast for REF Relay
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos |  | We have considered as per SLD
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos |  | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos |  | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | As per scheme | Nos |  | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos |  | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos |  | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos |  | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos |  | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme |  |  | MCB will be considered, Complied
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required | Considered
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos |  | Considered
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,Flush mount | Alstom |  | Nos |  | Considered
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos |  | Considered
| Earth fault inverse time over current (51G ) |  |  |  | Nos |  | Considered
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos |  | Considered
| Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos |  | Considered
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos |  | Considered
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer |  |  |  | Not Applicable
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos |  | Considered
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | As per scheme |  |  | Complied
Miscellaneous | Electronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos |  | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot |  | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos |  | Noted, Make ‐ Vaishno
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot |  | Complied
| Breaker handling /trolley |  | ABB/Siemens/Schneider | 1 | Nos |  | As per CRS total 4 nos breaker handling trolley shall be provided for complete package.
| Wire |  | Lapp | as per the design | lot |  | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot |  | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot |  | Complied
Bus bar | Busbar: 4000A Aluminium | [5 empty] | Main Horizontal Busbar sizes are selected as per BLOKSET Type Tested Assembly design which is in line with IEC Standards.The earth busbar shall be 1x50x5mm upto 50kA Panels and 2x50x5mm for above 50kA Panels.
PH: 3Rx180x10(AL.) Sq.mm
N: 2Rx180x10(AL.) Sq.mm
E: 1Rx125x10(AL.) Sq.mm
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Incomer 3200A (hidden)
BACK TO INDEX
Incomer 3200A
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 3200A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 3200A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 3200/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 3200/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 3200/1A, CL - PS, 20VA Resin cast for REF Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | As per scheme | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos
Relays | REF relay(64R) | REF relay(64R) | Alstom | as per scheme | Nos
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,Flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Breaker handling /trolley |  | ABB/Siemens/Schneider | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Bus bar | Busbar: 4000A Aluminium
PH: 3Rx180x10(AL.) Sq.mm
N: 2Rx180x10(AL.) Sq.mm
E: 1Rx125x10(AL.) Sq.mm
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Buscoupler 4000A
BACK TO INDEX
Buscoupler 4000A
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Remarks | Vendor Comments dt:
ACB | 4000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos |  | 4000A, 65kA, FP, MIC6.0E, ACB – MTZ Active‐ MTZ240H16.0E4PED
| 4000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos |  | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos |  | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos |  | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos |  | As required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
CT PT | Current Transformer | CT CTR: 4000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set |  | CT CTR: 3200/1A , Cl‐0.5, 20VA Resin cast ‐ metering
| Current Transformer | CT CTR: 4000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set |  | CT CTR: 3200/1A, CL ‐ 5P20, 20VA Resin cast for Protection Relay
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos |  | Not Applicable
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED | ABB/Siemens/Schneider | 1 | Nos |  | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos |  | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos |  | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos |  | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos |  | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos |  | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos |  | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos |  | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos |  | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos |  | Complied
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required | Not Applicable
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos |  | Not Applicable
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,with flush mount | Alstom |  | Nos |  | Considered
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos |  | Considered
| Earth fault inverse time over current (51G ) |  |  |  | Nos |  | Considered
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos |  | Considered
| Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos |  | Considered
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos |  | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot |  | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos |  | Complied, Make ‐ Vaishno
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot |  | Complied
| Wire |  | Lapp | as per the design | lot |  | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot |  | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot |  | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG 1250A ACB
BACK TO INDEX
OG 1250A ACB
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 1250A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1250A, 65kA, FP, MIC6.0E, EDO, ACB‐MTZ Active ‐ MTZ212H16.0E4PED
| 1250A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
CT PT | Current Transformer | CT CTR: 1250/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set | Not Applicable
| Current Transformer | CT CTR: 1250/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Complied
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | As required
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider |  |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos | Complied
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Relay | ELR | ELR with CBCT for 1000 A | ABB/Siemens/Schneider | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | As required
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG 1000A ACB
BACK TO INDEX
OG 1000A ACB
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 1000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1000A, 65kA, FP, MIC6.0E, EDO, ACB ‐MTZ ACTIVE‐MTZ210H16.0E4PED
| 1000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
CT PT | Current Transformer | CT CTR: 1000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set | Not Applicable
| Current Transformer | CT CTR: 1000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Complied
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | As required
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider |  |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos | Complied
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Relay | ELR | ELR with CBCT for 1000 A | ABB/Siemens/Schneider | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | As required
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG 315KW Soft starter
BACK TO INDEX
OG 315KW Soft starter Feeder
| Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
| ACB | 1000A 3P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1000A, 65kA, FP, MIC6.0E, EDO, ACB ‐ MTZ ACTIVE with ELR CBCT ‐ MTZ210H16.0E4PED
|  | 1000A 3P 65kA,MICRO PROCESS BASED OL,SC,EF release - LSIG | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
|  | ELR with CBCT for 800A |  | ABB/Siemens/Schneider | 1 | Nos
| ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Communication Interfacing for the breaker |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | As required
|  | MCB | 6A TPN 10kA MCB 'C' Curve | ABB/Siemens/Schneider | 1 | Nos | Noted
| Relay | Supervision relay | Trip circuit Supervision relay(95) | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | ELR | ELR with CBCT for 250 A | ABB/Siemens/Schneider | 1 | Nos | Complied
| Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
|  | Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
|  | Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| selector Switch | SS/Bypass selector switch | SS/Bypass selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | Local/remote for SS operation | Local/Remote selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | Local/remote for ACB operation | Local/Remote selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | MCB | 6A DP 10kA MCB 'C' Curve | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | TNC switch | TNC Switch,25A | Salzer | 1 | Nos | Noted
| Soft starter & Acc | Soft starter (SS) | 315 KW, Softstarter Supply Voltage Range: 200V AC to 480V AC, Control Voltage: 110 to 250V AC | ABB/Siemens/Schneider | 1 | Nos | 315KW Soft starter ATS490 660A 208 to 690VATS490C66Y
|  | Operating panel display unit of the soft starter | Required |  |  |  | Complied
|  | External display unit of SS on the door with communication cable | Required |  |  |  | Complied
|  | Motor protection Relay (MPR) | Simocode / LTMR / UMC | ABB/Siemens/Schneider |  |  | Complied
|  | Current measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Voltage measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Door mounted MPR display unit | Required | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Other special cables if any required | for internal & external communication | ABB/Siemens/Schneider | 1 | lot | Complied
|  | Semiconductor fuse with base | Sutable to the motor rating | ABB/Siemens/Schneider/Bussman | 3 | Nos | Complied
| Switch gear accessories | Power /Vaccum Contactor for Soft starter | Type 2 co ordinated, 3P AC3 duty for SS,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Power / Vaccum Contactor for DOL bypass | Type 2 co ordinated, 3P AC3 duty for Bypass,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Aux contactor | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Compled, as required
|  | Add on block | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Complied
|  | shrouding | As per IEC standard | Reputed | 1 | lot | Not Applicable as per BlokSet design
|  | IR window | Required | Fluke | 1 | Nos | Complied
|  | MCB | rating as per scheme | ABB/Siemens/Schneider | 1 | lot | Noted, As required
|  | Exhaust fans | As applicable | Fluke | As per scheme | Nos | Complied, EBM Make
| SS Indication | Indication lamp,flush type,110AC/DC,LED | ON | ABB/Siemen/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | OFF | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Noted
|  | MCB | OEM specs | ABB/Siemens/Schneider | 1 | Nos | Noted
| Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| Ammeter | Ammeter | Required | Reputed | 1 | Nos | Noted
|  | Ammeter selection switch | Required | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
| Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG 225KW Soft starter
BACK TO INDEX
OG 225KW Soft starter Feeder
| Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
| ACB | 1000A 3P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1000A, 65kA, FP, MIC6.0E, EDO, ACB ‐ MTZ ACTIVE with ELR CBCT ‐ MTZ210H16.0E4PED
|  | 1000A 3P 65kA,MICRO PROCESS BASED OL,SC,EF release - LSIG | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
|  | ELR with CBCT for 800A |  | ABB/Siemens/Schneider | 1 | Nos
| ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Communication Interfacing for the breaker |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | As required
|  | MCB | 6A TPN 10kA MCB 'C' Curve | ABB/Siemens/Schneider | 1 | Nos | Noted
| Relay | Supervision relay | Trip circuit Supervision relay(95) | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
|  | ELR | ELR with CBCT for 250 A | ABB/Siemens/Schneider | 1 | Nos | Complied
| Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
|  | Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
|  | Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| selector Switch | SS/Bypass selector switch | SS/Bypass selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | Local/remote for SS operation | Local/Remote selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | Local/remote for ACB operation | Local/Remote selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | MCB | 6A DP 10kA MCB 'C' Curve | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | TNC switch | TNC Switch,25A | Salzer | 1 | Nos | Noted
| Soft starter & Acc | Soft starter (SS) | 315 KW, Softstarter Supply Voltage Range: 200V AC to 480V AC, Control Voltage: 110 to 250V AC | ABB/Siemens/Schneider | 1 | Nos | 315KW Soft starter ATS490 660A 208 to 690VATS490C66Y
|  | Operating panel display unit of the soft starter | Required |  |  |  | Complied
|  | External display unit of SS on the door with communication cable | Required |  |  |  | Complied
|  | Motor protection Relay (MPR) | Simocode / LTMR / UMC | ABB/Siemens/Schneider |  |  | Complied
|  | Current measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Voltage measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Door mounted MPR display unit | Required | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Other special cables if any required | for internal & external communication | ABB/Siemens/Schneider | 1 | lot | Complied
|  | Semiconductor fuse with base | Sutable to the motor rating | ABB/Siemens/Schneider/Bussman | 3 | Nos | Complied
| Switch gear accessories | Power /Vaccum Contactor for Soft starter | Type 2 co ordinated, 3P AC3 duty for SS,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Power / Vaccum Contactor for DOL bypass | Type 2 co ordinated, 3P AC3 duty for Bypass,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | Aux contactor | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Compled, as required
|  | Add on block | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Complied
|  | shrouding | As per the IEC standard | Reputed | 1 | lot | Not Applicable as per BlokSet design
|  | IR window | Required | Fluke | 1 | Nos | Complied
|  | MCB | rating as per scheme | ABB/Siemens/Schneider | 1 | lot | Noted, As required
|  | Exhaust fans | As applicable | Fluke | As per scheme | Nos | Complied, EBM Make
| SS Indication | Indication lamp,flush type,110AC/DC,LED | ON | ABB/Siemen/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | OFF | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Noted
|  | MCB | OEM specs | ABB/Siemens/Schneider | 1 | Nos | Noted
| Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| Ammeter | Ammeter | Required | Reputed | 1 | Nos | Noted
|  | Ammeter selection switch | Required | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
| Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG 75KW Soft starter
BACK TO INDEX
OG 75KW Soft starter Feeder
| Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
| MCCB-MCCB - Drawout type,Double break mechanism | MCCB 250A 3P 65kA, MP based OL, SC, EF Release (LSIG) ,with display | Schneider : - CVS /NSX series ABB : - XT2/XT4/XT5 series Siemens : - 3VA2 series | ABB/Siemens/Schneider | 1 | Nos | 320A,3P,50kA, MCCB ‐ CVS ‐ MA TYPELV540552
|  | Aux & Alarm contact |  |  | 1 | Nos | Complied
|  | Handle |  |  | 1 | Nos | Complied
| Indication | Indication lamp,flush type,110AC/DC,LED | ON | ABB/Siemen/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | OFF | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Noted
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Noted
|  | MCB | 6A TPN 10kA MCB 'C' Curve | ABB/Siemens/Schneider | 1 | Nos | Noted
| Soft starter & Acc | Soft starter (SS) | 315 KW, Softstarter Supply Voltage Range: 200V AC to 480V AC, Control Voltage: 110 to 250V AC | ABB/Siemens/Schneider | 1 | Nos | 90KW Soft starter ATS480 210A 208 to 690V ‐ ATS480C21Y
|  | Operating panel display unit of the soft starter | Required |  |  |  | Complied
|  | External display unit of SS on the door with communication cable | Required |  |  |  | Complied
|  | Motor protection Relay (MPR) | Simocode / LTMR / UMC | ABB/Siemens/Schneider |  |  | Complied
|  | Current measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Voltage measuring module for MPR | Required | ABB/Siemen/Schneider | 3 | Nos | Complied, quantity as per scheme
|  | Door mounted MPR display unit | Required | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Other special cables if any required | for internal & external communication | ABB/Siemens/Schneider | 1 | lot | Complied
|  | Semiconductor fuse with base | Sutable to the motor rating | ABB/Siemens/Schneider/Bussman | 3 | Nos | Complied
| Switch gear accessories | Power /Vaccum Contactor for Soft starter | Type 2 co ordinated, 3P AC3 duty for SS,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Noted
|  | Power / Vaccum Contactor for DOL bypass | Type 2 co ordinated, 3P AC3 duty for Bypass,3NO+3NC | ABB/Siemens/Schneider | As per scheme | Nos | Noted
|  | Aux contactor | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Compled, as required
|  | Add on block | rating & qty as per scheme | ABB/Siemens/Schneider | 1 | lot | Complied
|  | shrouding | As per the standard | Reputed | 1 | lot | Not Applicable as per BlokSet design
|  | IR window | Required | fluke | 1 | Nos | Not Applicable
|  | MCB | rating as per scheme | ABB/Siemens/Schneider | 1 | lot | Noted, As required
|  | Exhaust fans | As applicable | Fluke | As per scheme | Nos | Complied, EBM Make
| selector Switch | SS/Bypass selector switch | SS/Bypass selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
|  | Local/remote | Local/Remote selecter switch,6A | SWITRON / Kaycee / Salzer | 1 | Nos | Noted
| SS Indication | Indication lamp,flush type,110AC/DC,LED | ON | ABB/Siemen/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
|  | Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
|  | MCB | OEM specs | ABB/Siemens/Schneider | 1 | Nos | Complied
| Relay | ELR | ELR with CBCT for 250 A | ABB/Siemens/Schneider | 1 | Nos | Complied
| Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Ameter | Ammeter | Required | Reputed | 1 | Nos | Complied
|  | Ammeter selection switch | Required | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Buscoupler 3200A (hidden)
BACK TO INDEX
Buscoupler 3200A
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Vendor Comments dt:
ACB | 3200A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 3200A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 3200/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 3200/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED | ABB/Siemens/Schneider | 1 | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos
Relays | REF relay(64R) | REF relay(64R) | Alstom | as per scheme | Nos
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,with flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## OG 800A ACB (hidden)
BACK TO INDEX
OG 800A ACB
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 800A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 800A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
CT PT | Current Transformer | CT CTR: 800/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 800/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Relay | ELR | ELR with CBCT for 1000 A | ABB/Siemens/Schneider | 1 | Nos
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire | As per the scheme | Lapp | 1 | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## OG 630A ACB (hidden)
BACK TO INDEX
OG 630A ACB
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 630A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 630A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
CT PT | Current Transformer | CT CTR: 630/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 630/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Relay | ELR | ELR with CBCT for 1000 A | ABB/Siemens/Schneider | 1 | Nos
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire | As per the scheme | Lapp | 1 | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Control trafo (hidden)
BACK TO INDEX
Category | Sub Category | Description | Make | Quantity | UOM

## OG 250 to 630A drawout Fdr MCCB
BACK TO INDEX
OG 250A to 630 A drawout Feeder
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
MCCB - Drawout type,Double break mechanism | 250A 4P FIXED PART, 65kA |  | ABB/Siemens/Schneider | 1 | Nos | Rating as per SLD
| 250A 4P MOVING Part ,65kA, MCCB,MICRO PROCESS BASED OL,SC,EF release - LSIG display | Schneider : - CVS /NSX series ABB : - XT2/XT4/XT5 series Siemens : - 3VA2 series | ABB/Siemens/Schneider | 1 | Nos | Complied with CVS MCCB
| Aux & Alarm contact |  | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Handle |  | ABB/Siemens/Schneider | As per scheme | Nos | Complied
Indication | Indication lamp,flush type,110AC/DC,LED | MCCB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Not Applicable
| Analog Ammeter, 96 x 96 mm, with selector switch for R,Y,B |  | Reputed Make | 1 | Nos | Complied
| CT CTR: xxx/1 A, Cl-0.5, 20VA Resin cast - metering | CTR - As applicable | Kalpa | 1 | Set | CT CTR: xxx/1 A, Cl-1, 10VA Resin cast - metering
Relay | ELR | ELR with CBCT for 250 A | ABB/Siemens/Schneider | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | As per scheme | lot | As required
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | As per scheme | lot | Noted, As required
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Wire make shall be as per OEM standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## OG <250A power FDR - MCCB
BACK TO INDEX
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
OG <250A power Feeder
MCCB - Drawout type,Double break mechanism | < 250A 4P , MCCB,65kA,MICRO PROCESS BASED OL,SC,EF release - LSIG with display | Schneider : - CVS /NSX series ABB : - XT2/XT4/XT5 series Siemens : - 3VA2 series | ABB/Siemens/Schneider | 1 | Nos | 100A, 50KA, 3P, TMD, MCCB ‐ C10N3TM100
| Aux & Alarm contact |  | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Handle |  | ABB/Siemens/Schneider | 1 | Nos | Complied
Indication | Indication lamp,flush type,110AC/DC,LED | MCCB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Not Applicable
| Analog Ammeter, 96 x 96 mm, with selector switch for R,Y,B |  | Reputed Make | 1 | Nos | Complied
| CT CTR: xxx/1 A, Cl-0.5, 20VA Resin cast - metering | CTR - As applicable | Kalpa | 1 | Set | CT CTR: xxx/1 A, Cl-1, 10VA Resin cast - metering
Relay | ELR | ELR with CBCT for 250 A | ABB/Siemens/Schneider | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | As per scheme | lot | As required
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | As per scheme | lot | Noted, As required
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Wire make shall be as per OEM standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Incomer 1250A IMCC
BACK TO INDEX
Incomer 1250A IMCC
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 1250A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1250A, 65kA, FP, MIC6.0E, EDO, ACB‐MTZ Active‐ MTZ212H16.0E4PED
| 1250A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | If required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | Complied
CT PT | Current Transformer | CT CTR: 1250/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Noted
| Current Transformer | CT CTR: 1250/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set | Not Applicable
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | We have considered as per SLD
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos | Not Comply
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider |  |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer |  |  | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE |  | Complied
Relay | Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos | Not Applicable as per SLD
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos | Complied
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer |  |  | Not Applicable
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE |  | Complied
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos | Noted, Make ‐ Vaishno
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Bus bar | Busbar: Aluminium |  |  |  |  | Complied
| PH: |  |  |  |  | Main Horizontal Busbar sizes are selected as per BLOKSET Type Tested Assembly design which is in line with IEC Standards.The earth busbar shall be 1x50x5mm upto 50kA Panels and 2x50x5mm
N:
E:
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Incomer 800A IMCC (hidden)
BACK TO INDEX
Incomer 800A IMCC
Category | Sub Category | Description | Make | Quantity per I/C | UOM
ACB | 800A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 800A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 800/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
| Current Transformer | CT CTR: 800/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE
Relay | Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire | As per the scheme | lapp | 1 | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Bus bar | Busbar: Aluminium
PH:
N:
E:
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Buscoupler 1250A IMCC
BACK TO INDEX
Buscoupler 1250A IMCC
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Vendor Comments dt:
ACB | 1250A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1250A, 65kA, FP, MIC6.0E, EDO, ACB‐MTZ Active‐ MTZ212H16.0E4PED
| 1250A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | If required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | Complied
CT PT | Current Transformer | CT CTR: 1250/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set | Not Applicable
| Current Transformer | CT CTR: 1250/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Noted
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | We have considered as per SLD
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED |  |  | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme |  | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Complied
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 |  | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 |  | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE | Nos | Considered
Relay | Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos | Not required as per SLD
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | lot | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | lot | Noted
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 |  | Noted
| Wire |  |  |  | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Noted
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 |  | Noted
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Incomer 1000A IMCC
BACK TO INDEX
Incomer 1000A IMCC
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
ACB | 1000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1000A, 65kA, FP, MIC6.0E, EDO, ACB ‐ MTZ ACTIVE with ELR CBCT ‐ MTZ210H16.0E4PED
| 1000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | If required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | Complied
CT PT | Current Transformer | CT CTR: 1000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Noted
| Current Transformer | CT CTR: 1000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set | Not Applicable
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | We have considered as per SLD
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider |  |  | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer |  |  | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE |  | Complied
Relay | Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos | Not required as per SLD
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos | Complied
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer |  |  | Not Applicable
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE |  | Complied
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos | Noted, Make ‐ Vaishno
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Bus bar | Busbar: Aluminium |  |  |  |  | Complied
| PH: |  |  |  |  | Main Horizontal Busbar sizes are selected as per BLOKSET Type Tested Assembly design which is in line with IEC Standards.The earth busbar shall be 1x50x5mm upto 50kA Panels and 2x50x5mm
N:
E:
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Buscoupler 1000A IMCC
BACK TO INDEX
Buscoupler 1000A IMCC
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Vendor Comments dt:
ACB | 1000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos | 1000A, 65kA, FP, MIC6.0E, EDO, ACB ‐ MTZ ACTIVE with ELR CBCT ‐ MTZ210H16.0E4PED
| 1000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos | Complied
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos | Complied
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | If required
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos | Complied
CT PT | Current Transformer | CT CTR: 1000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set | Not Applicable
| Current Transformer | CT CTR: 1000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set | Noted
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | We have considered as per SLD
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED |  |  | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Noted
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme |  | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos | Not Applicable
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Complied
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 |  | Complied
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos | Complied
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos | Digital Multifunction meter Cl:0.5 with Modbus RS485 communication
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos | Complied
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 |  | Complied
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE | Nos | Considered
Relay | Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos | Not required as per SLD
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | lot | Not Applicable
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | If required
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | lot | Noted
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 |  | Noted
| Wire |  |  |  | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Noted
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 |  | Noted
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Buscoupler 800A IMCC (hidden)
BACK TO INDEX
Buscoupler 800A IMCC
Category | Sub Category | Description | Make | Quantity per B/C | UOM
ACB | 800A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 800A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 800/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | set
| Current Transformer | CT CTR: 800/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED |  |  | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | To be decided during DDE | Nos
Relay | Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | lot
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | Nos
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | lot
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  |  |  | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## 55kW VFD
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
OG <200A power Feeder
MCCB - Drawout type,Double break mechanism | < 200A 4P , MCCB,65kA,MICRO PROCESS BASED OL,SC,EF release - LSIG with display | Schneider : - CVS /NSX series ABB : - XT2/XT4/XT5 series Siemens : - 3VA2 series | ABB/Siemens/Schneider | 1 | Nos | Complied with COMPACT NSX MCCB
| Aux & Alarm contact |  | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Handle |  | ABB/Siemens/Schneider | 1 | Nos | Complied
Indication | Indication lamp,flush type,110AC/DC,LED | MCCB ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | MCCB TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
VFD | VFD | Make | ABB/Siemens/Schneider | 1 | Nos | Schneider
| Application | Constant torque for water pumps | - | - | - | Noted
| Input voltage | 415 Voltage (+ 10 % -15% TPN) | - | - | - | Complied
| System frequency max | 50Hz ( +/- 5% ) | - | - | - | Complied
| Ambient temp | 50 deg Centigrade | - | - | - | Complied
| Derating to be considered | @ 50 deg C | - | - | - | Complied
| Short time over load | For Continous operation with 110% OL | - | - | - | Noted
| Input choke | To be considered as per rating of VFD | - | - | - | VFD has built-in DC Line choke hence external AC Line Coke is not considered
| Out put choke | To be considered as per rating of VFD | - | - | - | Complied
| Distance from drive to motor | > 500 m | - | - | - | Noted
| Invertor type | Diode front end (DFE) | - | - | - | Complied
| Drive model | Drive Selection based on Motor current( FLC) * 1.1 times continous current of the motor. Vendor to fill up format | - | - | - | Noted ATV630D75N4 shall be offered
| Total current harmonics PCC should be less than 5% at full load | should be less than 5% at full load. | - | - | - | Current THD at drive input is approx. 40%. Since the drives rating and quantity is very less the harmonics impact of these drives in overall system is very minimal. Hence as discussed we have not considered any harmonic filter.
| Drive display unit / control unit | Door mounted | - | - | - | Noted
| Current rating of the VFD module at 50 DegC for heavy duty | Drive Selection based on Motor current * 1.1 times continious current | - | - | - | Noted
| Control supply voltage | 110 Volts AC | - | - | - | Noted
| Aux contactor | 110 V AC 2NO+2NC Min 6 nos (As per scheme requirement ). Should provide Potential free contacts to integrate with PLC/DCS | - | - | - | Noted
| Semiconductor Fuse | To be considered as applicable | - | - | - | Noted
| MCCB ,Contactor and Aux contactor make | ABB / Siemens / Schneider only | - | - | - | Schneider
| Indicating lamps | ABB / Siemens / Schneider only | - | - | - | Schneider
| Control transformer | To be considered as applicable | - | - | - | Noted
| Enclosure protection | IP54 | - | - | - | IP42
| Door locks and Hinges | T type hand operated heavy duty door locks and heavy duty Hinges | - | - | - | Complied
| LOTO provision at Main Incomer isolator | Provision shall be provided for Incoming MCCB | - | - | - | Complied
| Phase barriers / Enclosures for exposed parts | Should provide safety secured barriers at MCCB and out going cable termination end . All exposed busbars and transformers and connections should be enclosed | - | - | - | Complied
| Outgoing bus bars - termination accessories | Cadmium coated, bolts with 2 plain washer and 1 spring washer will be sent with the panels. These will be In the outgoing busbar holes, not sent loose. | - | - | - | Zinc coated shall be provided
| Digital inputs | Minimun 6 nos | - | - | - | Complied
| Digital outputs | Minimun 6 nos | - | - | - | Complied
| Analog inputs ( 4-20mA) | Minimun 2 nos | - | - | - | Complied
| Analog outputs 4-20 mA Isolated | Minimun 2 nos | - | - | - | Complied
| Signal Isolator | As applicable | - | - | - | Complied
| Communication protocol | Ethernet IP/Profinet compatible | - | - | - | Ethernet IP
| DCS integration | Signals will be soft communicable as well hardwired to Plant PLC / DCS | - | - | - | Complied
| VFD wiring scheme ,status indications and bus bars | As per specification | - | - | - | Noted
| Hardwiring provision | For Start, Stop, E-Stop, Speed ref, Current feedback LCS signals to be considered as per sample drawing | - | - | - | Noted
| Conformal coating | 3C3 standard | - | - | - | Complied
| Enclosure dimensions | with 75 mm base channel maximum height of the panel shall be restricted to 2300 mm | - | - | - | Complied
| Enclosure sheet steel thickness | 2 mm for Load bearing and 1.6 mm for Non load bearing | - | - | - | 2 mm for Load bearing and 1.5 mm for Non load bearing
| Enclosure Cabinet cooling fan | Suitable fan with control MCB shall be installed in the enclosure with louvers | - | - | - | Complied
| Enclosure illumination | suitable wattage panel illumination with its control shall be provided | - | - | - | Complied
| Enclosure gland plate | Un drilled suitable size CRCA steel with 3 mm thick | - | - | - | Complied
| 2 years spares to be quoted | As per 2 years spares list | - | - | - | Shall be as per "04_V_SGB_PMCC_IMCC_Schneider_2 Year Spares"
| LCS to be quoted | For each VFD LCS shall be considered stainless steel 304 grade sheet enclosure with suitable size of 5 mm thick Aluminium Gland plate - should quote seperately | - | - | - | Not Applicable.
| Supervision of erection and commissioning | As per separate annexure | - | - | - | Noted
| DOL bypass option to be provided | To be provided as per given DOL specs | - | - | - | Noted
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## DOL < 75KW
BACK TO INDEX
DOL < 75KW
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
MCCB - Drawout type,Double break mechanism | MCCB 250A 3P 65kA, MP based OL, SC, EF Release (LSIG) ,with display | Schneider : - CVS /NSX series ABB : - XT2/XT4/XT5 series Siemens : - 3VA2 series | ABB/Siemens/Schneider | 1 | Nos | Rating as per BOM (Index)
| Aux & Alarm contact |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Handle |  | ABB/Siemens/Schneider | 1 | Nos | Complied
Relay | ELR |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Special cables | internal communication between MPR & PLC | ABB/Siemens/Schneider | 1 | lot | Cable for MPR to display
| CBCT |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| MPR with DI,DO etc as per JSW spec | Motor Protection Relay | ABB/Siemens/Schneider | 1 | Nos | Complied, DI, DO etc shall be as concluded wrt coimments/clarification sheet
Miscellaneous | MPR display unit on the door | to be provided in each phase. | ABB/Siemens/Schneider | 1 | Nos | Complied for MPR display unit
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | As required
| Current module | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | As required
| Voltage module | As per the scheme | ABB/Siemen/Schneider | 1 | Nos | Considered
| 250A, 3P, 110V AC, Power Contactor with AC coil, Aux. Contact 2NO+2NC, | As per the scheme | ABB/Siemen/Schneider |  |  | Power contactor selection will be as per type 2 co‐ordination chart
Indication | Indication lamp,flush type,110AC/DC,LED | On ON | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | off OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider |  |  | Not Applicable
| Test Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | As required
| Power Contactor/Vaccum contactor | Rating during DDE Vaccum contactor for motor feeders >= 45kW | ABB/Siemen/Schneider | As per the scheme | Nos | Complied Vaccum contactor for motor feeders >= 55kW
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## RDOL < 5KW
BACK TO INDEX
RDOL < 5KW
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Vendor Comments dt:
MPCB | MPCB 6A 3P 50kA, MP based OL, SC. | Rating during DDE | ABB/Siemens/Schneider | 1 | Nos | Rating as per BOM (Index)
| Aux & Alarm contact |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Handle |  | ABB/Siemens/Schneider | 1 | Nos | Complied
Relay | ELR |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| Special cables | Internal communication between MPR & PLC | ABB/Siemens/Schneider | 1 | lot | Cable for MPR to display
| CBCT |  | ABB/Siemens/Schneider | 1 | Nos | Complied
| MPR with DI,DO etc as per JSW spec | LTMR/UMC/Simocode | ABB/Siemens/Schneider | 1 | Nos | Complied, DI, DO etc shall be as concluded wrt coimments/clarification sheet
Miscellaneous | MPR display unit on the door | As applicable | ABB/Siemens/Schneider | 1 | Nos | Complied
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | As required
| Current module | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | Integral with controller upto 100A, above 100A external CT is used
| Voltage module | As per the scheme | ABB/Siemens/Schneider | 1 | Nos | Considered
| 250A, 3P, 110V AC, Power Contactor with AC coil, Aux. Contact 2NO+2NC, |  |  |  |  | Power contactor selection will be as per type 2 co‐ordination chart
Indication | Indication lamp,flush type,110AC/DC,LED | Fwd On | ABB/Siemen/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | off OFF | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | rev On | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | TRIP | ABB/Siemens/Schneider | 1 | Nos | Complied
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos | Complied
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD, shrouded type | ABB/Siemens/Schneider | As per scheme | Nos | Complied
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Test Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos | Not Applicable
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos | Complied
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot | As required
| Power Contactor for both FWD & REV | Rating during DDE |  | As per the scheme | Nos | Complied
| Aux contactors for Valve torque & valve position feedback |  |  |  |  | Complied
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot | Complied
| Wire | As per the scheme | Lapp | 1 | lot | Noted, Make of wires shall be as per Manufacturer standard
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot | Complied
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot | Complied
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme |  | Refer Sr No. 47 of Annexure A Comments Clarification Sheet

## Comm & Misc
BACK TO INDEX | Communication and Miscellemous items
Comm & Misc
Category | Sub Category | Description | Make | Quantity | UOM | Vendor Comments dt:
Power supply unit | Fanless type SMPS for 24VDC for communication modules | I/P supply - 85-230VAC O/P -24VDC O/P current min 10A to be considered | Siemens / Weidemuller / Phoenix | 2 nos per bus section | Set
| Diode O ring module |  | Pheonix or equivalent | 1 nos per bus section | Nos
N/W Item | Ethernet switch 24 port | a) 1 GBPS 4 nos uplink port,24 port RJ45 ports b) Redundant unmanaged switch required | hurshman / Moxa / Phoenix / Cisco | Qty as per 20% spare ports for each swicth after all connections | Nos
| Machine crimped ethernet / Profinet cable- Cat 6 E | Length as per the requirement | Phoenix/Schneider/Molex/Siemens | As per the requirement | Mtr
| Industrial grade RJ45 Connectors |  | Phoenix/Schneider/Molex | As per the scheme | Nos
PLC | PLC for changeover | 6 nos spare DI & 6 nos spare DO to be available | ABB/Siemens/Schneider | one per PMCC | Nos
HMI | HMI for PLC | HMI for PLC | ABB/Siemens/Schneider | one per PMCC | Nos
Busbar Temperature | Monitoring System | a) Zigbee based System b) HMI for the system to be provided on the panel door. c) Communication with Plant PLC over Ethernet required | ABB/Siemens/Schneider | one per PMCC | Set
MPR Display |  | a) Panel door mounted display required. b) Connecting cable should be in proper cable tray | ABB/Siemens/Schneider | one per MPR | Nos
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## OG 630A ACB Feeder
BACK TO INDEX
OG 630A ACB
Category | Sub Category | Description | Make | Quantity per I/C | UOM
ACB | 630A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 630A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
CT PT | Current Transformer | CT CTR: 630/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 630/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Local / Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Relay | ELR | ELR with CBCT for 630 A | ABB/Siemens/Schneider | 1 | Nos
Miscellaneous | Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire | As per the scheme | Lapp | 1 | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Incomer 1600A
BACK TO INDEX
Incomer 1600A
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Remarks | Vendor Comments dt:
ACB | 1600A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 1600A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | As per scheme
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 1600/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 1600/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 1600/1A, CL - PS, 20VA Resin cast for REF Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | As per scheme | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,Flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Miscellaneous | Electronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Breaker handling /trolley |  | ABB/Siemens/Schneider | 1 | Nos
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Bus bar | Busbar: 1600A Aluminium (size to be confirmed by vendor)
PH: (size to be confirmed by vendor)
N: (size to be confirmed by vendor)
E: (size to be confirmed by vendor)
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Buscoupler 1600A
BACK TO INDEX
Buscoupler 1600A
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Remarks
ACB | 1600A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 1600A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 1600/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 1600/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED | ABB/Siemens/Schneider | 1 | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,with flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Incomer 2000A
BACK TO INDEX
Incomer 2000A
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Remarks | Vendor Comments dt:
ACB | 2000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 2000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | As per scheme
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 2000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2000/1A, CL - PS, 20VA Resin cast for REF Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | As per scheme | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,Flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Miscellaneous | Electronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Breaker handling /trolley |  | ABB/Siemens/Schneider | 1 | Nos
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Bus bar | Busbar: 2000A Aluminium (size to be confirmed by vendor)
PH: (size to be confirmed by vendor)
N: (size to be confirmed by vendor)
E: (size to be confirmed by vendor)
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Buscoupler 2000A
BACK TO INDEX
Buscoupler 2000A
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Remarks
ACB | 2000A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 2000A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 2000/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2000/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED | ABB/Siemens/Schneider | 1 | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,with flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Incomer 2500A
BACK TO INDEX
Incomer 2500A
Category | Sub Category | Description | Make | Quantity per I/C | UOM | Remarks | Vendor Comments dt:
ACB | 2500A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 2500A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | As per scheme
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 2500/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2500/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2500/1A, CL - PS, 20VA Resin cast for REF Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | As per scheme | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,Flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay | Reputed Make | 1 | Nos
control Transformer | Control transformer for ACB control circuit | Control transformer 415/110V AC for ACB control circuit CL:1 Resin cast type 415/110V AC,insulation class H,rating as per the requirement | Kalpa | 1 | Nos
| Control trafo selector switch - trafo 1/2/independent / off | suitable to the scheme | SWITRON / Kaycee / Salzer
| Control transformer for Bus section | Control transformer 415/110V AC for space heater CL:1 Resin cast type 415/110V AC,insulation class H,Rating will be desided to catter the load of all bus section | Kalpa | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with 65kA with magnetic release suitable rating to be considered | ABB/Siemens/Schneider | As per scheme
Miscellaneous | Electronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Breaker handling /trolley |  | ABB/Siemens/Schneider | 1 | Nos
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Bus bar | Busbar: 2500A Aluminium (size to be confirmed by vendor)
PH: (size to be confirmed by vendor)
N: (size to be confirmed by vendor)
E: (size to be confirmed by vendor)
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme

## Buscoupler 2500A
BACK TO INDEX
Buscoupler 2500A
Category | Sub Category | Description | Make | Quantity per B/C | UOM | Remarks
ACB | 2500A 4P FIXED PART, 65kA | EMax2 / 3WA / MTZ | ABB/Siemens/Schneider | 1 | Nos
| 2500A 4P MOVING Part LSIG with E-Kip touch release | EMax2 E-Kip / 3WA ETU 600 / MTZ MIC 6.0E | ABB/Siemens/Schneider | 1 | Nos
ACB Acc | Shunt Opening -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Shunt Closing -110V AC |  | ABB/Siemens/Schneider | 1 | Nos
| Door interlock - Right and left-hand side of chassis |  | ABB/Siemens/Schneider | 1 | Nos
| EDO Motors |  | ABB/Siemens/Schneider | 1 | Nos
| Mechanical operating counter |  | ABB/Siemens/Schneider | 1 | Nos
| 4NO+4NC Aux contacts |  | ABB/Siemens/Schneider | 1 | Nos
| POWER SUPPLY UNIT FOR ACB DISPLAY, ETHERNET MODBUS TCP IP-110-240V AC/DC |  | ABB/Siemens/Schneider | 1 | Nos
| AUP contact (Position contact) |  | ABB/Siemens/Schneider | 1 | Nos
| Padlock accessory (LOTO at ACB ON/OFF Push Button) |  | ABB/Siemens/Schneider | 1 | Nos
| PLP Supplementary lock Key lock and padlock in racked-in / test / racked-out position |  | ABB/Siemens/Schneider | 1 | Nos
| Castle Key Interlock with lock & mounting kit |  | ABB/Siemens/Schneider | 1 | Nos
| Safety shutters |  | ABB/Siemens/Schneider | 1 | Nos
| BSCM ( Breaker Status and Control Module) |  | ABB/Siemens/Schneider | 1 | Nos
| Ready to close signalling contact- RTC |  | ABB/Siemens/Schneider | 1 | Nos
| Communication Interfacing for the breaker |  | Modbus TCP IP / Profinet / Ethernet IP | 1 | Nos
Line PT | Potential Transformere's | Potential Transformer 415/rt3/110V/rt3, 3 Phase CL:1.0, 50VA | Precise / Kalpa | 1 | Nos
| MPCB | MPCB with TM Based O/C & S/C Rel., 1NO+1NC Aux., Cont.,rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
| MCB | MCB , 10kA MCB 'C' Curve,type & rating as per the requirement | ABB/Siemens/Schneider | As per scheme | Nos
CT PT | Current Transformer | CT CTR: 2500/1A , Cl-0.5, 20VA Resin cast - metering | Kalpa | 1 | Set
| Current Transformer | CT CTR: 2500/1A, CL - 5P20, 20VA Resin cast for Protectiorn Relay | Kalpa | 1 | Set
Indication | Indication lamp,flush type,110AC/DC,LED | ACB ON | ABB/Siemen/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB OFF | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TRIP | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB TCH | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Spring Charging | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Upstream breaker healthy | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Test Position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Service position | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | ACB Ready to Close | ABB/Siemens/Schneider | 1 | Nos
| Indication lamp,flush type,110AC/DC,LED | any additional if required as per scheme | ABB/Siemens/Schneider | As per scheme | Nos
| Indication lamp,flush type,110AC/DC,LED | Sync permitted lamp,flush type,110AC/DC,LED | ABB/Siemens/Schneider | 1 | Nos
| MCB | MCB | ABB/Siemens/Schneider | As per scheme | Nos
| Annuciation Window | 12 Window Annunciator, Aux., Supply : 85-270VAC/DC | Minilec | 1 | Nos
Push Buttons | Push Button emergency | RED/2NC+2NO, TYPE-TURN TO RELEASE/MUSHROOM HEAD,shrouded type | ABB/Siemens/Schneider | As per scheme | Nos
| Reset | Fault Acknowledge | ABB/Siemens/Schneider | As per scheme | Nos
| Test | Test Push Buttons | ABB/Siemens/Schneider | As per scheme | Nos
| Test lamp | for Lamp test ,2NO+2NC | ABB/Siemens/Schneider | 1 | Nos
| Push Button | BLACK/2NO+2NC, TYPE-SPRING RETURN/FLUSH | ABB/Siemens/Schneider | As per scheme | Nos
selector Switch | TNC | 32A,Type-CAM,2 NO+2NC,with Pisol Grip Handle, spring return,3 pole 2 way | Salzer | 1 | Nos
| Auto / Manual / Individual / Momentory Parallel | 4 way Switch | SWITRON / Kaycee / Salzer | 1 | Nos
| Local Remote | 2 NO+2NC , 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| selection switch | if any this missing in this BOM & required for scheme to be considered | SWITRON / Kaycee / Salzer | As per scheme | Nos
Metering | MFM | Digital Multifunction meter Cl:0.5 with ,Modbus TCP IP / Ethernet IP/communication | Schneider - PM5560/EM7290 / Siemens - PAC 3200 | 1 | Nos
| Voltmeter | Analog AC Voltmeter, CL : 1.0 (96x96mm) (0-600)V | Reputed Make | 1 | Nos
| Voltmeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter selector switch | Rating 16A | SWITRON / Kaycee / Salzer | 1 | Nos
| Ammeter | Analog AC Ammeter, CL : 1.0 (96x96mm),range as per the suitable rating | Reputed Make | 1 | Nos
| Isolation at both I/C & O/G side to be considered | MCB / MPCB with suitable rating to be considered | ABB/Siemens/Schneider | As per scheme | Nos
Relays | REF relay(64R) | REF relay(64R) | Alstom | As per scheme | Nos | Electromechanical Relay required
| Standby Earth fault Relay -SE/F | E/F Relay(Standby Earth fault ) | Alstom |  | Nos
| Master Trip Relay(86) | Master Trip Relay(86) with 4NO+4NC,with flush mount | Alstom |  | Nos
| Trip Circuit Supervision Relay - (95) | Trip Circuit Supervision Relay | Alstom |  | Nos
| Earth fault inverse time over current (51G ) |  |  |  | Nos
| Under Voltage (27) & Over voltage (59) Relay | Under Voltage Relay | Alstom |  | Nos
| Check Synchronising Relay | Check Synchronising Relay,85-230VAC,with built in synchroscope,Voltage & frequency LED indication,with 2NO+2NC ,Flush mounting type | Reputed Make | 1 | Nos
Miscellaneous | Eletronic timer | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Add on blocks | As per the scheme | ABB/Siemens/Schneider | 1 | lot
| ELECTRONIC TYPE BUZZER | voltage: 85-230VAC | Reputed Make | 1 | Nos
| Aux contactors | As per the scheme, No interposing relay to be considered ,only contactor to be considered | ABB/Siemens/Schneider | 1 | lot
| Wire |  | Lapp | as per the design | lot
| 3ph,4W Test Terminal Block, screw type | As per the scheme | Reputed Make | 1 | lot
| TYPE-32A / Neutral Link Disconnecting | As per the scheme | Reputed Make | 1 | lot
Special Note | If any item missing in this BOM & same required during the DDE shall be considered without any price implications |  |  | As per scheme