## Load list
Description | W/S | Type (DOL/VFD/Feeder) | Amps rating (A) | kW rating (kW) | Voltage level (V) | Duty/standby group
Boiler feed water pump A (duty) | W | DOL |  | 185 | 433 | BFW
Boiler feed water pump B (standby) | S | DOL |  | 185 | 433 | BFW
Cooling water pump A (duty) | W | DOL |  | 160 | 433 | CWP
Cooling water pump B (standby) | S | DOL |  | 160 | 433 | CWP
ID fan | W | VFD |  | 250 | 433 | Boiler
ID fan | W | VFD |  | 250 | 433 | Boiler
ID fan | S | VFD |  | 250 | 433 | Boiler
FD fan | W | VFD |  | 200 | 433 | ESP
FD fan | W | VFD |  | 200 | 433 | ESP
FD fan | S | VFD |  | 200 | 433 | ESP
Air compressor | W | DOL |  | 132 | 433
Conveyor 1 | W | DOL |  | 90 | 433
Conveyor 2 | W | VFD |  | 75 | 433
Crusher | W | DOL |  | 315 | 433
Dosing pump (amps only) | W | DOL | 180 |  | 433
Booster fan (amps only) | W | VFD | 120 |  | 433
Lighting & small power DB | W | Feeder | 250 |  | 433
MCC-2 incomer | W | Feeder | 800 |  | 433
Grinding mill | W | DOL |  | 450 | 690
Slurry pump | W | VFD |  | 355 | 690
HGMS 2 Feed Pump 1 | W | VFD |  | 250 | 433 | HGMS2 Feed Pump
HGMS 2 Feed Pump 2 | W | VFD |  | 250 | 433 | HGMS2 Feed Pump
HGMS 2 Feed Pump 3 | W | VFD |  | 250 | 433 | HGMS2 Feed Pump
HGMS 2 Feed Pump 4 | S | VFD |  | 250 | 433 | HGMS2 Feed Pump
Warman slurry pump for Stirred Mill-1 | S | VFD |  | 110 | 433
HGMS 1 Feed Pump 1 | W | VFD |  | 250 | 433 | HGMS1 Feed Pump
HGMS 1 Feed Pump 2 | W | VFD |  | 250 | 433 | HGMS1 Feed Pump
HGMS 1 Feed Pump 3 | W | VFD |  | 250 | 433 | HGMS1 Feed Pump
HGMS 1 Feed Pump 4 | S | VFD |  | 250 | 433 | HGMS1 Feed Pump
Thickener 1 Feed Pump 1 | W | VFD |  | 200 | 433 | Thickener1 Feed Pump
Thickener 1 Feed Pump 2 | W | VFD |  | 200 | 433 | Thickener1 Feed Pump
Thickener 1 Feed Pump 3 | W | VFD |  | 200 | 433 | Thickener1 Feed Pump
Thickener 1 Feed Pump 4 | S | VFD |  | 200 | 433 | Thickener1 Feed Pump
Thickener 2 Feed Pump 1 | W | VFD |  | 275 | 433 | Thickener2 Feed Pump
Thickener 2 Feed Pump 2 | W | VFD |  | 275 | 433 | Thickener2 Feed Pump
Thickener 2 Feed Pump 3 | W | VFD |  | 275 | 433 | Thickener2 Feed Pump
Thickener 2 Feed Pump 4 | S | VFD |  | 275 | 433 | Thickener2 Feed Pump
MCC-3 incomer | W | Feeder | 550 |  | 433
MCC-4 incomer | W | Feeder | 700 |  | 433
MCC-5 incomer | W | Feeder | 900 |  | 433

## Notes
How the load list is read
Only the first sheet ('Load list') is read. Keep the header row; column order does not matter.
kW given -> motor of that kW. kVA = kW / (power factor x efficiency).
Only amps given and Type is DOL or VFD -> motor. kVA = sqrt(3) x V x A.
Only amps given and Type is anything else -> outgoing feeder. kVA = sqrt(3) x V x A.
Power factor: DOL 0.7, VFD 0.9, feeder 0.7. Efficiency 95 %. All loads at 100 % (standby included).
Voltage level: 433 or 690 (volts). Rows that do not match the selected transformer are listed as excluded.
Duty/standby group (optional): loads with the same group name are placed on different transformers' bus sections.
Optional columns can be left out; extra columns are ignored.
The values in this file are examples only.