## Load list
Description | W/S | Type (RDOL/DOL/VFD/SS/Feeder) | Amps rating (A) | kW rating (kW) | Voltage level (V) | Duty/standby group
Tailing Thickener Flocculant Dosing & Preparation System | W | Feeder | 139.2855 | 70 | 433 | BFW
Tailing Thickener Rack mechanism | W | Feeder | 99.4896 | 50 | 433 | BFW
Tailing Thickener Transfer Pump 1A |  | Feeder | 14.9234 | 7.5 | 433 | CWP
Tailing Thickener Transfer Pump 1B |  | Feeder | 14.9234 | 7.5 | 433 | CWP
Tailing Thickener Transfer Pump - Spare |  | Feeder | 14.9234 | 7.5 | 433 | Boiler
Tailing Thickener Dosing Pump 1A |  | Feeder | 9.352 | 4.7 | 433 | Boiler
Tailing Thickener Dosing Pump 1B |  | Feeder | 9.352 | 4.7 | 433 | Boiler
Tailing Thickener Dosing Pump Spare |  | Feeder | 9.352 | 4.7 | 433 | ESP
Tailing Thickener Mixing Tank Agitator |  | Feeder | 4.3775 | 2.2 | 433 | ESP
Tailing Thickener Mixing Tank Agitator - Spare |  | Feeder | 4.3775 | 2.2 | 433
Tailing Paste Thickener |  | Feeder | - | - | 433
Intermediate Thickener Mixing Tank Agitator - Spare |  | Feeder | 4.3775 | 2.2 | 433
Rake Lift |  | DOL | 2.1888 | 1.1 | 433
Intermediate Thickener Rack mechanism | Spare | Feeder | 99.4896 | 50 | 433
Intermediate Thickener Flocculant Dosing & Preparation System | Spare | Feeder | 99.4896 | 50 | 433
DE WATERING PUMP1 | W | Feeder | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-1 | Spare | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-2 | w | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-3 | w | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump- spare | Spare | DOL | 59.6938 | 30 | 433
Seal water pump (Tailing)-1 | w | VFD | 85.1189 | 55 | 433
Pump house Electric hoist - 1 | w | Feeder | 59.6938 | 30 | 433
pump house sump area Electric hoist - 2 | Spare | Feeder | 59.6938 | 30 | 433
Chiller AHU-1 | w | Feeder | 21.8877 | 11 | 433
Chiller AHU spare | Spare | Feeder | 21.8877 | 11 | 433
Motorised value-1 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433
Motorised value-2 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433
Motorised value-3 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433
Tailing Thickener Flocculant Dosing & Preparation System | Spare | Feeder | 139.2855 | 70 | 433
Tailing Thickener Rack mechanism | Spare | Feeder | 99.4896 | 50 | 433
Intermediate Thickener Rack mechanism | w | Feeder | 99.4896 | 50 | 433
Intermediate Thickener Flocculant Dosing & Preparation System | w | Feeder | 99.4896 | 50 | 433
Intermediate Thickener Transfer Pump 1B |  | Feeder | 13.9285 | 7 | 433
Intermediate Thickener Transfer Pump - Spare |  | Feeder | 13.9285 | 7 | 433
Intermediate Thickener Dosing Pump 1A |  | Feeder | 4.9745 | 2.5 | 433
Intermediate Thickener Dosing Pump 1B |  | Feeder | 4.9745 | 2.5 | 433
Intermediate Thickener Dosing Pump Spare |  | Feeder | 4.9745 | 2.5 | 433
DE WATERING PUMP2 | w | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-4 | w | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-5 | w | DOL | 59.6938 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump-6 | w | VFD | 46.4285 | 30 | 433
Pump house Pit pump for spilled slurry pumping pump- spare | Spare | DOL | 59.6938 | 30 | 433
Seal water pump (Tailing)-2 | S | VFD | 85.1189 | 55 | 433
Seal water pump (Tailing) spare | Spare | VFD | 85.1189 | 55 | 433
pump house sump area Electric hoist - 1 | w | Feeder | 59.6938 | 30 | 433
Pump house Electric hoist - 2 | Spare | Feeder | 59.6938 | 30 | 433
Chiller AHU-2 | W | Feeder | 21.8877 | 11 | 433
Chiller AHU-3 | W | Feeder | 21.8877 | 11 | 433
Motorised value-4 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433
Motorised value-5 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433
Motorised value-6 for exesting system to SGB | w | RDOL | 4.3775 | 2.2 | 433

## Notes
How the load list is read
Only the first sheet ('Load list') is read. Keep the header row; column order does not matter.
kW given -> motor of that kW. kVA = kW / (power factor x efficiency).
Only amps given and Type is DOL or VFD -> motor. kVA = sqrt(3) x V x A.
Only amps given and Type is anything else -> outgoing feeder. kVA = sqrt(3) x V x A.
Power factor: DOL 0.7, VFD 0.9, feeder 0.7. Efficiency 95 %. All loads at 100 % (standby included).
Voltage level: 433 or 690 (volts). Rows that do not match the selected transformer are listed as excluded.
Duty/standby group (optional): loads with the same group name are placed on different transformers' bus sections.
Optional columns can be left out; extra columns are ignored.
The values in this file are examples only.